## Sheet1
No. | Category | Question | POC | Response | Answered
57 | Software & Licensing | Cloud services vs on-premises requirement. Please confirm whether any cloud-hosted services are permitted for security, AV, or IT systems, or if all systems (VMS, access control, AV control, recording, etc.) must be entirely on-premises within NNSS networks due to security policies. | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
56 | Software & Licensing | Software and license responsibility summary. Across the security and AV scopes there will be software platforms and licenses (VMS, access control, SAS, AV control software, VTC codecs, etc.). Please provide a matrix indicating, for each software platform: • Required vendor/product and version, • Whether licenses are owner-furnished or contractor-furnished, and • Which party is responsible for installation, configuration, and ongoing support. | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
55 | Testing, Commissioning & Warranties | Cybersecurity and hardening requirements. Are there specific cybersecurity standards (e.g., FIPS 140-2, NIST, site-specific hardening guides) that field devices (cameras, access panels, AV codecs, etc.) must meet, and is the network and device hardening effort to be included in this contract? | Michael Dako | Any cyber security/ hardening requirement wouldn’t apply to the contractor. MSTS Physical Security Systems (PSS) department installs all the physical security systems at the NNSS. The contractor is only responsible for installing infrastructure (i.e., conduit, junction boxes, enclosures) to support the PSS systems. | Yes
54 | Testing, Commissioning & Warranties | Integration testing with NNSS IT and PSS. The PRS requires integrated facility controls and communications systems to be grounded, coordinated, and operational, but does not clearly describe who performs final integration with existing NNSS IT/PSS infrastructure. Please clarify whether the LV contractor should include time for: • Onsite support to NNSS IT for switch configuration, VLAN assignments, WAP provisioning, • Onsite support to PSS for camera and access control enrollment into Milestone/ACS, and • Participation in integrated functional testing and end-to-end demonstrations. | BMcD | The Division 27 subcontractor is not required to perform functional testing of the networking or security equipment as this will be Owner performed. The Division 27 subcontractor shall perform the testing outlined in the Structured Cabling specifications. | Yes
53 | Testing, Commissioning & Warranties | Structured cabling certification and installer qualifications. IT standards call for a Siemon Certified System with 20-year warranty and specific test methods (Fluke DTX or equivalent). Please confirm that: • The structured cabling contractor must be a Siemon-certified installer authorized to issue the manufacturer’s warranty, and • Whether a similar manufacturer-backed warranty is required for Corning fiber. | BMcD | The Division 27 subcontractor shall be Siemon certified system installer. The standard Corning manufacturers warranty is acceptable and the contractor must have any required Corning certifications. | Yes
52 | Pathways, Sleeves, Cable Tray & Penetrations | Penetrations and firestopping for low-voltage systems. For penetrations between fire/smoke or security compartments (PPA, LA, VTR, SAS), please confirm whether: • Division 27 is expected to core drill and firestop its own penetrations, or • Penetrations and firestopping will be provided by others, with Division 27 only routing through provided sleeves. |  | have some parts that could be addressed in the agreements between MSTS and the Unions and some parts which may need to be determined between the GC and sub-tier. | Yes
51 | Pathways, Sleeves, Cable Tray & Penetrations | Trade responsibility for cable tray and ladder rack. The PRS and IT standards specify minimum sizes for cable tray/ladder rack and grounding requirements, and Division 27 lists rack and ladder manufacturers, but it is unclear whether Division 26 or Division 27 is responsible for installing main signal cable tray and sleeves in corridors and above ceilings. Please clarify which division is responsible for: • Main corridor cable tray and telecommunication sleeves, • Ladder racks within TRs, and • Grounding of trays/racks. |  | have some parts that could be addressed in the agreements between MSTS and the Unions and some parts which may need to be determined between the GC and sub-tier. | Yes
50 | Drawings vs Specs & Device Counts | Updated room name/number coordination. To correctly assign data, AV, and security outlets, please confirm that a final coordinated room name and number matrix (matching architectural, IT, and security drawings) will be issued prior to construction, or provide it now for estimating purposes. |  | IFC's are now available | Yes
49 | Drawings vs Specs & Device Counts | Reconciliation of device counts between drawings and program. The PRS and programming tables describe functional requirements (badge readers at all entry doors, cameras at all entries and parking areas, PA throughout, etc.), while device-by-device counts will be shown on discipline drawings. Please confirm that: • The construction drawings will be updated, if necessary, to fully reflect all programmed devices, and • Our bid should be based on the final issued drawings and schedules, not on narrative counts alone. |  | IFC are now available. Confirmed - bids will be based on IFC's | Yes
48 | Audio/Video (AV) & Public Address / Mass Notification | PA/MNS integration with fire alarm and VoIP systems. The fire alarm spec lists Notifier as the basis-of-design, and Section 27 51 16 covers PA/MNS installation and testing, with references to telephone paging. Please clarify: a) Is the PA/MNS system required to integrate with the fire alarm for voice evacuation and/or priority paging, and who is responsible for the interface hardware and programming on each side? b) Is paging through the VoIP system (PBX integration) in scope for the LV contractor, and are there any PBX brand/compatibility constraints we must allow for? | BMcD | The Paging System is required to interface with the VoIP telephone system via a VoIP inteface module as shown on the Paging Riser Diagram. All VoIP equipment shall be Owner provided. BMCD | Yes
47 | Audio/Video (AV) & Public Address / Mass Notification | Required AV control platform and programming responsibility. Are there NNSS-standard AV control platforms (e.g., Crestron, Extron, AMX) and user interface templates that must be used? If so, please confirm: • Required manufacturer, • Who provides control software licenses, and • Whether the LV/AV contractor is responsible for programming and commissioning these systems. | Jacob Ruben - MSTS | • Required manufacturer: Response - The Standard is Extron • Who provides control software licenses: Response - We (MSTS) would handle control licenses • Whether the LV/AV contractor is responsible for programming and commissioning these systems: Response - We (MSTS) would program the system. | Yes
46 | Audio/Video (AV) & Public Address / Mass Notification | AV equipment vs infrastructure scope split. The PRS states the Construction Subcontractor shall “purchase and install Video teleconferencing (VTC) equipment (TVs, microphones, all-in-one systems, etc.)” and that IT equipment and standards must be coordinated with IT PMO. Please provide a room-by-room AV equipment list indicating which items are: • Contractor-furnished and installed (displays, codecs, DSPs, microphones, speakers, AV switches, control processors, etc.), and • Owner-furnished (e.g., certain PCs, collaboration endpoints), so we can accurately estimate material and programming. | Jacob Ruben - MSTS | IFC's are now available - Jacob Ruben can provide the list; however, he just received the IFC's as well. | Yes
45 | CCTV / Security Video | Armory 20/20 and Door Guard systems scope. For Building 23-473, the PRS requires infrastructure for “Armory 20/20” and “Door Guard” systems. 0025220-CC-26_Project Requirement Please clarify: • Is the contractor to furnish and install these proprietary systems (including controllers, software, and integration to PSS/Milestone), or • Only provide raceway, cabling, power, and network connections to support installation by others? | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
44 | CCTV / Security Video | Camera models, performance, and environmental requirements. Specs and PRS describe CCTV coverage needs (doors, parking, façade, interior), but do not clearly define required camera resolutions, lensing, or environmental ratings. 0025220-CC-26_Project Requirement Please provide or confirm minimum performance criteria (e.g., pixel density at target, day/night capability, WDR, vandal/weather ratings) and whether there is a standard NNSS camera family that must be used. | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
43 | CCTV / Security Video | Milestone VMS scope (licenses, servers, and storage). The PRS requires that cameras be tied into the PSS Milestone network, with special references to OCC wildland cameras and monitoring. Please clarify whether the contractor’s scope includes: • Milestone server hardware, VMS licenses, and storage arrays, • Client workstations/monitors for monitoring locations, and • Configuration/integration of all new cameras into the existing Milestone system, or if these items are entirely owner-furnished, with the contractor providing only network and power infrastructure plus camera devices. | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
42 | Access Control Scope & Manufacturers | SAS / LA intrusion and access control scope. The SAS requirements describe IDS and ACS performance standards and reference DOE O 473.1A, including two-factor authentication, logging, and CCTV monitoring. Please clarify whether: • All SAS/LA IDS devices (door contacts, BMS switches, PIRs, tamper alarms) and access control components are part of the Division 28 scope under this contract, or • Whether any SAS IDS and ACS elements will be provided by PSS under a separate contract, with this project only providing conduits and cabling. | BMcD | All security equipment will be Owner provided under a separate contract. All security (ESS) scope includes infrastructure only to support the security systems. | Yes
41 | Access Control Scope & Manufacturers | Door hardware and access control responsibility matrix. For all doors requiring access control, please provide (or confirm forthcoming) a schedule that clearly assigns responsibility (hardware vendor vs Division 08 vs Division 26 vs Division 27) for: • Card readers, keypads, REX devices, DPS contacts, • Electrified locks/maglocks, power supplies, batteries, enclosures, and • Fire alarm interlocks and door release interfaces. This will allow us to avoid overlapping scope and ensure all required components are included. | BMcD | Division 08 is responsible for all door hardware and Division 26 is responsible for conduit, backboxes, power, and grounding in coordination with the Division 27 subcontractor. | Yes
40 | Access Control Scope & Manufacturers | Access control system platform and ownership. The PRS states “Access control and alarm systems will be designed by the M&O Contractor’s Physical Security Systems (PSS) group” and calls for badge readers on all building entry doors and secure areas. Please identify the required access control platform (e.g., LenelS2 or other NNSS standard) and clarify whether: • Controller hardware and software licenses are owner-furnished or part of this contract, and • The LV contractor must provide programming and database configuration, or only field wiring and terminations. | BMcD | Security (ESS) scope includes infrastructure only which includes conduit, backboxes, power, and grounding as shown on the drawings. | Yes
39 | PoE Powering & Switch Capacity | Responsibility for PoE switches. The IT standards reference switch configurations (e.g., Extreme switches) but also state network equipment is owner-furnished. Please confirm that all PoE switches required to power WAPs, cameras, access control panels, IP speakers, and other PoE devices are owner-furnished/installed, and that Division 27 provides only cabling and patching to those switch ports. | BMcD | All active network switching equipment shall be provided by the Owner. | Yes
38 | PoE Powering & Switch Capacity | Identification of all PoE loads. The PRS and specs require Wi-Fi, VoIP, cameras, access control, and AV infrastructure but do not clearly identify which devices are PoE-powered vs locally powered. Please provide a list or design directive indicating which device types are intended to be PoE-powered so we can correctly estimate switch port counts and cabling. | BMcD | The Division 27 contractor is not responsible for switch port counts as this equipment shall be supplied by the Owner. Assume all cabling may include PoE to the endpoint for bundling / cabling heating mitigations. | Yes
37 | HVAC / EMCS / BAS Network Cabling & Other PoE – Your direct question | TR UPS integration with BAS. TR requirements state that all TR UPS units shall be capable of being connected to the BAS, while IT standards cover grounding and integrated controls. Please clarify whether Division 27 must: • Provide only network cabling interfaces from TR UPS equipment to BAS/EMCS panels, or • Also include any signal cabling (dry contacts, analog/digital I/O) needed for UPS status monitoring. | BMcD | The Division 27 subcontractor include only network intefaces from TR UPS equipment. | Yes
36 | HVAC / EMCS / BAS Network Cabling & Other PoE – Your direct question | PoE cabling for non-IT systems (HVAC, lighting, specialty devices). With PoE increasingly used for BAS controllers, lighting control devices, and specialty sensors, please confirm: a) Should Division 27 provide PoE cabling and terminations for any and all PoE devices in the project, regardless of discipline? b) Or is Division 27’s PoE cabling limited to traditional IT endpoints (data outlets, WAPs, VoIP phones, cameras, intercoms), with HVAC/lighting vendors responsible for their own PoE circuits? | BMcD | The Division 27 subcontractor cabling is limited to what is shown on the Telecommunications drawings. | Yes
35 | HVAC / EMCS / BAS Network Cabling & Other PoE – Your direct question | Division 27 responsibility for HVAC / EMCS network cabling. Section 25 55 00 (EMCS) and 23 09 23 (DOC for HVAC) describe the controls architecture and BACnet/EMCS requirements, but do not clearly assign responsibility for the Ethernet / IP network cabling between DDC controllers, data acquisition panels, and the building network. Please clarify whether Division 27 is to include or exclude: • Network copper/fiber cabling between HVAC/EMCS panels and telecom rooms, • Any BAS controllers or gateways that reside on the IT network, and • Any cross-building BAS fiber that may be required. | BMcD | The Division 27 subcontractor is not responsible for the Division 25 scope unless specific BAS or Metering outlets have been shown on the Telecommunications drawings. | Yes
34 | Structured Cabling & Telecom Scope | Patch cables: quantities and responsibility. Table 11 specifies detailed Black Box and Siemon patch cable part numbers and color-coding by network (blue, gray, green, white). Please clarify: a) Are all TR and workstation patch cords in the IT standards to be supplied and installed under Division 27, or by the Owner/IT? b) If by Division 27, should we include only initial patching or a spare stock (and at what percentage)? | BMcD | The Division 27 subcontractor shall supply all patch cords and station cords for the project. Provide any spare stock as required by the specifications. | Yes
33 | Structured Cabling & Telecom Scope | Owner-furnished network equipment vs contractor scope. The PRS indicates “data network system equipment (routers, switches) are owner furnished and installed” and that PBX/VoIP head-end and telephones are also owner-furnished. Please confirm that the low-voltage/telecom contractor is not to include: • Network switches, routers, firewalls, wireless controllers, or • PBX/VoIP servers or handsets, and is limited to cabling, patch panels, racks, labeling, and testing. | BMcD | Confirmed. All active networking equipment and voice equipment shall be Owner furnished. | Yes
32 | Structured Cabling & Telecom Scope | 16. Extent of Division 27 structured cabling scope. The PRS states the Construction Subcontractor shall “install conduit, pull wires/fiber, terminate wires/fiber, and splice all IT infrastructure needed to meet the equipment requirements.” 0025220-CC-26_Project Requirements Please confirm that Division 27 is responsible for all structured cabling (copper and fiber) for: • General IT (data, voice, Wi-Fi, VoIP), • Security (access control, CCTV, SAS connectivity), and • AV and VTC systems, unless specifically noted otherwise. | BMcD | The Division 27 subcontractor is responsible for the Structured Cabling System. The security (ESS) scope is rough-in only including boxes, conduits, power, and grounding. The Audio/Video scope may be performed by the same Division 27 subcontractor if that contractor call meet all the quality assurance requirements of the AV specifications, otherwise another subcontractor will be necessary. | Yes
31 | General / Manufacturers & Substitutions | Priority between Project Manual and PRS IT standards. Section 27 10 00 lists “available manufacturers” for fiber (Corning) and UTP (Siemon) and accessories, while the PRS Table 11 appears to set stricter NNSS standards and specific part numbers. Please clarify which document has precedence when there is a conflict (e.g., part numbers, cable colors, rack styles). | BMcD | The Division 27 specification shall take precedence for this project. | Yes
30 | General / Manufacturers & Substitutions | Siemens vs Siemon naming conflict. The PRS requires a “Siemon Certified System, 20 Year Warranty” for structured copper cabling, but also references “Siemens manufacturer’s instructions” and a “Siemens certificate” for testing and optical fiber. Please confirm: a) Is Siemon the required structured cabling manufacturer, and b) Are all references to “Siemens” in the IT standards intended to read “Siemon”, or do they refer to a different required product line? | BMcD | Siemon is the required Structured Cabling manufacturer and all references to "Siemens" is actually referencing "Siemon". | Yes
29 | General / Manufacturers & Substitutions | Are listed manufacturers “closed spec” or “or equal”? The PRS “NNSS IT Standards and Requirements” and Division 27 list very specific manufacturers and part numbers for structured cabling, racks, patch cords, jacks, etc. (Siemon, Corning, Chatsworth, Black Box, Dymo, Panduit, APC, etc.). Please confirm whether these are mandatory manufacturers (closed spec), or if equivalent products are acceptable. If equivalents are allowed, please describe the approval process and any pre-approved alternate vendors. | BMcD | The Division 27 specifications list specific manufacturer model numbers that meet the NNSS IT Standards and the requirement for a Siemon certified structured cabling system. For equipment listed with multiple manufacturers, one of those listed manufacturers may be proposed by the contractor. | Yes
28 |  | When does MSTS anticipate the 100% design drawings will be available? | Jeff Moya MSTS | They are available as of 1.6.26 and will be sent out | Yes
27 |  | Will the PRIME provide as-built drawings if we redline the drawings? | Kirsten Staton | o Lower Tier Sub: completes final as-built/as-constructed shop drawings and calculations for delegated design submittals and issues to the GC Subcontractor. o GC Subcontractor: Captures all in-field changes not already included in the latest design document revisions as clear red-lined mark-ups, then issues those and their lower tier’s as-builts to the Contractor/DOR (Burns & McDonnell). o DOR: Validates and incorporates the red-lined changes from the GC and applicable information from the lower tier as-built submittals into a complete and final set of as-built design documents and issues to the Contractor for record. | Yes
26 |  | The Statement of Work references the 23-463 IFC Design Package and Drawing Number 023-463. There is no Electrical legend page with general and specific notes included in the 90% drawings. Electrical page missing for the MDSB panel schedule. No lighting fixture schedule is provided. Will these missing items be available prior to bid submission? | Jeff Moya | 100% IFC is now available | Yes
25 |  | Who is responsible for the Mandrel test of spare conduits? | Dexter Lee & Jimmy Stuart MSTS | should provide the document name/number/section they are asking about which would help identify who needs to provide the response. | Yes
24 |  | Will CONTRACTOR need to hire the independent NETA accredited testing agency be required to test the Main Switchboards, Feeders, and Grounding System? | Dexter Lee & Jimmy Stuart MSTS | should provide the document name/number/section they are asking about which would help identify who needs to provide the response. | Yes
23 |  | Is this tax exempt? | Calvin Callahan - Buyer | MSTS is not Tax Exempt | Yes
22 |  | Temporary Power: Is AGENCY providing all temporary power items, main temp service drop, and temporary distribution? We are assuming the CONTRACTOR does not need to cover the cost of power consumption. | Dexter Lee & Jimmy Stuart MSTS | should provide the document name/number/section they are asking about which would help identify who needs to provide the response. | Yes
21 |  | Seismic Bracing and Study: Who will hire the engineer to sign off on seismic bracing and related items? | Dexter Lee & Jimmy Stuart MSTS | should provide the document name/number/section they are asking about which would help identify who needs to provide the response. | Yes
20 |  | Coordination Study: Will CONTRACTOR need to hire an engineer to perform the short circuit, coordination’s, and Arc Flash Study before ordering the gear? Section 26 05 73 | Dexter Lee & Jimmy Stuart MSTS | Please provide clarification. CONTRACTOR is typically MSTS, SUBCONTRACTOR is typically the "prime contractor", and Sub-Tier is anyone hired by the SUBCONTRACTOR. Please re-send question using this logic. | Yes
19 |  | Are there design requirements from the SUBCONTRACTOR? | Jeff Moya MSTS | Yes - Burns & McDonnell is the Engineer of Record | Yes
18 |  | Conference rooms 106, 107 and 126 call for STC 45 rated doors and stub-outs for card-readers. Do the exterior walls need to meet SCIF requirements also, plans do not show a hard deck ceiling for these conference rooms? | BMcD | There are no SCIF requirements within the project scope, Rooms 106, 107 and 126 must test to meet an STC 45 rating. | Yes
17 |  | Does the Lighting Protection require a UL Certification? | Stirling Davis | Either a UL Certification or LPI certification is acceptable. | Yes
16 |  | If ACM is acceptabl, would the Government allow a proposal that maintains the existing floor plan while utilizing ACM in order to meet the 12-month Period of Performance | Jeff Moya | No, the ProtoSTAR specification and subsequent design must be followed. | Yes
15 |  | Will the Government and Burns & McDonnell (as the preparer of the 90% drawings) review and approve the use of ACM should it meet all functional,performance, and compliance requirements? | Jeff Moya | No, the ProtoSTAR specification and subsequent design must be followed. | Yes
14 |  | If ACM is permitted, will a proposal incorporating this method be fully considered during evaluation? | Jeff Moya | No, the ProtoSTAR specification and subsequent design must be followed. | Yes
13 |  | Would the Government allow the use of Alternative Construction Method in lieu of conventional construction to support an expidited delivery | Jeff Moya | No, the ProtoSTAR specification and subsequent design must be followed. | Yes
12 |  | Does the construction fencing need to have privacy/windscreen on it? | BMcD | No privacy/windscreen is required. -E. Watruba, 01-05-26 | Yes
11 |  | Who is responsible for performing GPR Activities? | BMcD | MSTS will mark their existing utilities prior to construction. Construction Subcontractor is responsible for any additional GPR, potholing, or utility locating services beyond the initial MSTS marking. -E. Watruba, 01-05-26 | Yes
10 |  | Will MSTS be providing building pads within 1' of building finish floor elevations as they have done in the past? | BMcD | No, see Civil drawings for grading requirements. -E. Watruba, 01-05-26 | Yes
9 |  | Have the building sites been over-exed and built back up by MSTS? | BMcD | No, see Civil drawings and specifications for over-excavation requirements. -E. Watruba, 01-05-26 | Yes
8 |  | How does the current administrations Executive Orders (EO) rolling back sustainability requirements for Federal Buildings and Projects affect the requirement for energy metering in the Project Requirements & Specifications (PRS) requirements for energy metering. Is energy metering stil desired/required? Please advise? |  | Must follow current PRS requirements | Yes
7 |  | Will temporary construction offices and storage containers require a permit to be onsite and used? If so, please provide the permitting process documentation and forms. Will any third party engineering be required for the placement of these office and storage containers? Please advise. | Kirsten Staton | as of today we are no longer requiring the construction trailer form or needing the BAP to review installation for a permit. They will still need to meet all site requirements for construction trailers that are spread through the other CDs but making sure that happens will be the responsibility of the PM and STR. | Yes
6 |  | In the specifications, multiple acceptable manufacturers are listed for electrical equipment. Confirm it is permissable to mix and match components manufacturers - such as conduit, straps, connectors - as long as each item meets the specified standards. Need to ensure all items do not need to meet one manufacturer as it would affect pricing schedule. | Stirling Davis & BMCD | mix and matching components is acceptable provided they meet the specified standards. The manufacturers listed were not meant to apply to componenents like conduit, straps, connectors, etc. - Stirling Davis Confirmed. It is acceptable to utilize multiple component manufacturers as described within question 6. - BMcD | Yes
5 |  | 023-463-E7006 - Exterior lighting fixtures include bollard lighting - 023-463-L-1010 shows sidewalks and landscaping plan, but quantity of bollard lighting is not depicted in drawings - please provide for accurate pricing | BMCD | Please refer to DRWG 023-463-E-1001. Confirm quantity is 50 lighted bollards. | Yes
4 |  | 023-463-E-4001 - 400A main shown - verify 400A service is acceptable for current and future use - 300KVA XMFR supports larger main. | BMCD | Concur. 400A main is intended. | Yes
3 |  | 26 05 19 - 3.01 D, "Feeders:Copper for feeders No. 4/0 AWG and smaller; copper or aluminum for feeders 250KCMIL and larger: - Verify aluminum conductors are acceptable over 250KCMIL. | Stirling Davis & BMCD | Must propose and use copper per MSTS Power Ops. | Yes
2 |  | Attachment 8 PLA agreement ends 9/30/2025 - Please provide new PLA wage agreement for accurate pricing. | Buyer - Calvin Callahan | Updated PLA was provided in Amendment 05. Attachments 08 and 09 of the solicitation | Yes
1 |  | 26 22 13 - 2.02 E, "Provide aluminum primary and secondary windings" - Verify aluminum windings are acceptable. | Stirling Davis - MSTS BMCD | Must propose and use copper per MSTS Power Ops. | Yes